## Slide 1: The Flow of Power
Simons Institute: Real-time Decision Making Bookcamp
Power Systems, Berkeley, January 2018
Steven Low
Notes: Simons Institute for the Theory of Computing, Berkeley
Program on Real-time Decision Making, Jan – May 2018
Organizers: Richard Karp (UCB, Chair), Josh Bloom (UCB), Steven Low (Caltech), Evdokia Nikolova (UTAustin), Balaji Prabhakar (Stanford)
Jan 25, 2018: Real-time Decision Marking Bootcamp: Energy Networks: The flow of Power, Berkeley (Karp)

## Slide 2: Bootcamp: Power systems
The flow of power (S Low)
  Basic concepts and models
  Power flow and optimization
The flow of information (S Meyn)
  Distributed control architectures
The flow of money (K Poolla)
  Market structures and services
from steady state to dynamics
from engineering to economics

## Slide 3: R. Karp’s instruction
“... the level should be sufficiently elementary that an expert on the topic will be bored.”

## Slide 4: The flow of power I
Why smart grid? (15 mins)
Three-phase AC transmission: 3 key ideas (30 mins)
  Phasor representation
  Balanced operation
  Per-phase analysis
Device models (30 mins)
  Transmission line
  Transformer
  Generator
Basic concepts and models

## Slide 5: The flow of power II
Network models (10mins)
  Admittance matrix
  Power flow models
Optimal power flow problems (35mins)
  Formulation and example
  Convex relaxations
  Real-time OPF
Power flow and optimization

## Slide 6: Why smart grid?

## Slide 7: Watershed moment
Bell: telephone
1876
Tesla: multi-phase AC
1888
both started as natural monopolies
both provided a single commodity
both grew rapidly through two WWs
1980-90s
1980-90s
deregulation
started
deregulation
started
Energy network will undergo similar architectural
transformation that phone network went through
in the last two decades to become the world’s
largest and most complex IoT
IoT
1969: DARPAnet
convergence
to Internet

## Slide 8: Watershed moment
Industries will be restructured
  AT&T, MCI, McCaw Cellular, Qualcom
  Google, Facebook, Twitter, Amazon, eBay, Netflix
Infrastructure will be reshaped
  Centralized intelligence, vertically optimized
  Distributed intelligence, layered architecture

## Slide 9: Watershed moment
(April 20, 2017)
What will drive power network transformation ?

## Slide 10: Watershed moment
(April 20, 2017)
What will drive power network transformation ?

## Slide 11: Electricity gen & transportation
They consume the most energy
  Consume 2/3 of all energy in US (2014)
They emit the most greenhouse gases
  Emit >1/2 of all greenhouse gases in US (2014)
To drastically reduce greenhouse gases
  Generate electricity from renewable sources
  Electrify transportation
Source:
USEPA
Notes: Source: LLNL, https://flowcharts.llnl.gov/content/assets/images/charts/Energy/Energy_2015_United-States.png
Source: USEPA, https://www3.epa.gov/climatechange/ghgemissions/sources/transportation.html

## Slide 12
World energy stats (2011)
Consumption | 519 quad BTU
petroleum | 34%
coal | 29%
gas | 23%
renewable (elec) | 8%
nuclear | 5%
Consumption | 519 (quad BTU) | per capita (mil BTU)
China | 20% | 78
US | 19% | 313
Russia | 6% | 209
India | 5% | 20
Japan | 4% | 164
total | 54% | 
top 5
countries
Source: EIA

## Slide 13
World energy stats (2011)
Consumption | 519 (quad BTU) | CO2 emission
China | 20% | 27%
US | 19% | 17%
Russia | 6% | 5%
India | 5% | 5%
Japan | 4% | 4%
total | 54% | 58%
top 5
countries
Consumption | 519 quad BTU
petroleum | 34%
coal | 29%
gas | 23%
renewable (elec) | 8%
nuclear | 5%
Source: EIA

## Slide 14
Source: USEPA, https://www3.epa.gov/climatechange/ghgemissions/sources/transportation.html
Total (2014) = 6,870 Million Metric Tons of CO2 equivalent
US greenhouse gas emission 2014
Electricity generation
and transportation are
top-two GHG emitters
(56% total)
… and they consume
the most energy
(66% total)

## Slide 15
US energy flow 2015
Source: LLNL, https://flowcharts.llnl.gov/content/assets/images/charts/Energy/Energy_2015_United-States.png

## Slide 16
US energy flow 2014
Source: EIA Monthly Energy Review March 2015
quadrillion BTU

## Slide 17: US electricity flow 2014
Source: EIA March 2015
Monthly Energy Review
Conversion loss:
63%
quadrillion Btu
Plant use: 2%
T&D losses: 2.4%
Gross gen:
37%
Nuclear: 21%
Renewable: 13%
US total energy use: 98.3 quads
For electricity gen: 39%
Fossil : 65%
End use:
33%

## Slide 18
US dirty supply
all fossils
nuclear
hydro
coal
gas
nuclear
wind
solar
hydro
oil
trillion kWh
2
1
billion kWh
coal
gas
Source:
US EIA
Notes: Coal consumption is decreasing while gas is going up. We can see from the monthly plots that they are almost crossing each other.
Nuclear generation has been relatively steady at around 20%
So is hydro at around 8% or so.
Wind is picking up in the last decade (2005-2015), but is still relatively small
Solar doesn’t even register at this scale. So let’s blow up the statistics on the renewables.

## Slide 19
Source: US EIA
US renewable generations
750 billion kWh
500
250
hydro
wind
nuclear
solar
Chart: 
hydro
wind
solar
Notes: Look at the monthly numbers, with hydro as the reference at about 8%.
Wind is approaching gas generation
Solar is picking up in the last couple years (2013-2015), but remains small.
Yet, the levelized cost of solar generation has been dropping dramatically in the last 5 years or so (2010 – 2015) as technologies advance and the industry scales. The cost is now under $3/watt and installed capacity by mid 2015 is close to 23 GW.
New startups with innovative business models have sprung up in the last couple years. In CA,

## Slide 20
US wind generation capacity exceeded hydro capacity in 2016
US wind capacity
Hydro capacity (2015):
78,956 MW
Wind capacity (2016):
82,183 MW

## Slide 21
Source: SEIA 2015
(Solar Energy Industries Association)
US solar capacity
US solar industry snapshot
  US installed solar capacity by mid 2015: ~23 GW
    784K homes and businesses
  Q2 2015 solar installation: 1.4 GW
    Utility: 729 MW
    Residential: 473 MW (70% growth yr-on-yr)
  H1 2015: a new solar installation / 2 mins
Federal
incentives
extended
to 2023

## Slide 23
Source: Renewable Energy
Global Status Report, 2010
Source: M. Jacobson, 2011
Wind power over land (exc. Antartica)
70 – 170 TW
Solar power over land
340 TW
Worldwide
energy demand:
16 TW
electricity demand:
2.2 TW
Notes: World wind speed at 100m:
All wind worldwide: 1,700 TW
All wind over land in high-wind areas outside Antartica: 70 – 170 TW
World power (all energy) demand in 2030: 16.9 TW
World surface solar
All solar worldwide: 6,500 TW
All solar over land in high-solar locations: 340 TW
Source: Renewable Energy Global Status Report, Sept 2010:
2009 grid-tied solar PV capacity increase
The world added 7GW of grid-connected PV capacity, to a total of 21 GW
Germany: +3.8 GW to a total of 9.8 GW
Spain: +70MW to a total of 3.4 GW (Govt subsidy expired!)
US: +470MW to a total of 1 GW (CA ~half of increase)
Off-grid capacity: 4 GW
2009 wind capacity increase
Wind power increased the most among all renewables, by 38 GW to a total of 159 GW
US: +10 GW to a total of 35 GW
China: +13.8 GW to a total of 25.8 GW
Germany: +1.9GW to a total of 25.8 GW

## Slide 24
Power the world by solar
Notes: World wind speed at 100m:
All wind worldwide: 1,700 TW
All wind over land in high-wind areas outside Antartica: 70 – 170 TW
World power (all energy) demand in 2030: 16.9 TW
World surface solar
All solar worldwide: 6,500 TW
All solar over land in high-solar locations: 340 TW
Source: Renewable Energy Global Status Report, Sept 2010:
2009 grid-tied solar PV capacity increase
The world added 7GW of grid-connected PV capacity, to a total of 21 GW
Germany: +3.8 GW to a total of 9.8 GW
Spain: +70MW to a total of 3.4 GW (Govt subsidy expired!)
US: +470MW to a total of 1 GW (CA ~half of increase)
Off-grid capacity: 4 GW
2009 wind capacity increase
Wind power increased the most among all renewables, by 38 GW to a total of 159 GW
US: +10 GW to a total of 35 GW
China: +13.8 GW to a total of 25.8 GW
Germany: +1.9GW to a total of 25.8 GW

## Slide 25: Uncertainty
High Levels of Wind and Solar PV Will Present an Operating Challenge!
Source: Rosa Yang, EPRI

## Slide 26
Source: Leon Roose, University of Hawaii
Development & demo of smart grid inverters for high-penetration PV applications
Voltage violations are quite frequent

## Slide 27
Source: Leon Roose, University of Hawaii
Development & demo of smart grid inverters for high-penetration PV applications
“Energiewende”

## Slide 28: Today’s grid
Few large generators
  ~10K bulk generators (>90% capacity), actively controlled
Many dump loads
  131M customers, 3,100 utilities, ~billion passive loads
Control paradigm: schedule supply to match demand
  Centralized, human-in-the-loop, worst case, deterministic

## Slide 29: Future grid
Wind and solar farms are not dispatchable
  Many small distributed generations
Network of distributed energy resources (DERs)
  EVs, smart buildings/appliances/inverters, wind turbines, storage
Control paradigm: match demand to volatile supply
  Distributed, real-time feedback, risk limiting, robust

## Slide 30
Risk: active DERs introduce rapid random
fluctuations in supply, demand, power quality
increasing risk of blackouts
Opportunity: active DERs enables realtime
dynamic network-wide feedback control,
improving robustness, security, efficiency
Caltech research: distributed control of networked DERs
Foundational theory, practical algorithms, concrete
applications
Integrate engineering and economics
Active collaboration with industry

## Slide 31: Implication of active DER
Current control paradigm works well today
  Centralized, open-loop, human-in-loop, worst-case preventive
  Low uncertainty, few active assets to control
  Schedule supplies to match loads
Future needs
  Closing the loop, e.g. real-time DR, volt/var
  Fast computation to cope with rapid, random, large fluctuations in supply, demand, voltage, freq
  Simple algorithms to scale to large networks of active DER
  Market mechanisms to incentivize

## Slide 32: Recap
Global energy demand will continue to grow
There is more renewable energy than the world ever needs
  Someone will figure out how to capture and store it
There will be connected intelligence everywhere
  Cost of computing, storage, communication and manufacturing will continue to drop
Power system will transform into the largest and most complex Internet of Things
  Generation, transmission, distribution, consumption, storage

## Slide 33: Recap
To develop technologies that will enable and guide the historic transformation of our power system
  Materials, devices, systems, theory, algorithms
  Control, optimization, stochastics, data, economics

## Slide 34: Motivation: Optimal power flow
describes network topology and impedances
is net power injection (generation) at node j
power flow equation
gen cost, power loss
line flow
injection limits
line limits
voltage limits

## Slide 35: The flow of power I
Why smart grid? (15 mins)
Three-phase AC transmission: 3 key ideas (30 mins)
  Phasor representation
  Balanced operation
  Per-phase analysis
Device models (30 mins)
  Transmission line
  Transformer
  Generator
Basic concepts and models

## Slide 36: Visualizing the grid

## Slide 38
Transmission lines: 190K miles
Distribution lines: 73K miles
(2002)
[Sascha von Meier]

## Slide 39
[Sascha von Meier]

## Slide 40: Today’s grid
Few large generators
  ~10K bulk generators (>90% capacity), actively controlled
Many dump loads
  131M customers, 3,100 utilities, ~billion passive loads
Control paradigm: schedule supply to match demand
  Centralized, human-in-the-loop, worst case, deterministic

## Slide 41
[Sascha von Meier]
Notes: 41

## Slide 42
service drop
[Sascha von Meier]
Notes: 42

## Slide 43
transmission
line
transmission
substation
[Sascha von Meier]
Notes: 43

## Slide 44
distribution
substation
[Sascha von Meier]
Notes: 44

## Slide 45
transformer &
distribution line
[Sascha von Meier]
Notes: 45

## Slide 46
service drop
[Sascha von Meier]
Notes: 46

## Slide 47: Mathematical model
Quantities of interest
  Voltage, current, power, energy
  All are sinusoidal functions of time
Voltage
  Steady state: frequencies at all points are nominal
  Reasonable model at timescale of minute and up
nominal frequency
US: 60 Hz
EU: 50 Hz

## Slide 48: Mathematical model
Quantities of interest
  Voltage, current, power, energy
  All are sinusoidal functions of time
Voltage
  Steady state: frequencies at all points are nominal
  Reasonable model at timescales of minute and up
  Dynamic models at sec-min timescale: S Meyn’s tutorial
nominal frequency
North/Central Americas: 60 Hz
Most other major countries: 50 Hz
this part of tutorial is all about steady state

## Slide 49: Phasor representation
Quantities of interest
  Voltage, current, power, energy
  All are sinusoidal functions of time
Voltage
amplitude
phase
voltage
phasor

## Slide 50: Phasor representation
Quantities of interest
  Voltage, current, power, energy
  All are sinusoidal functions of time
Voltage
voltage
phasor

## Slide 51: Phasor representation
Quantities of interest
  Voltage, current, power, energy
  All are sinusoidal functions of time
Voltage
voltage
phasor

## Slide 52: Phasor representation
Voltage
Current

## Slide 53: Linear circuit elements
Resistor R
Inductor L
Capacitor C
these are main circuit elements to model the grid

## Slide 54: Linear circuit elements
Resistor R
Inductor L
Capacitor C

## Slide 55: Linear circuit elements
time
domain
phasor
domain

## Slide 56: Complex power
Quantities of interest
  Voltage, current, power, energy
  All are sinusoidal functions of time
Instantaneous power
average power

## Slide 57: Complex power
Quantities of interest
  Voltage, current, power, energy
  All are sinusoidal functions of time
Instantaneous power
Complex power
real (active) power
average power
reactive power

## Slide 58: Phasor analysis
Steady state behavior described by algebraic equations
  Instead of dynamic equations
Circuit analysis
  Voltages and currents are linear
Power flow analysis
  Power flow equations are nonlinear
We will describe device and network models, and analyze
them, in phasor domain

## Slide 59: 3-phase AC : 3 key ideas
  Phasor representation
  Balanced operation
  Per-phase analysis

## Slide 60: 3-phase AC system
3 single-phase system:
single 3-phase system:

## Slide 61: 3-phase AC system
Y-configuration:
Delta-configuration:
voltage source
impedance load

## Slide 62: 3-phase AC system
Y-configuration:
voltage source
impedance load
Balanced 3p source
  Equal in magnitude, 120 deg difference in phase
Balanced 3p impedance load
  Identical impedances

## Slide 63: 3-phase AC system
Delta-configuration:
voltage source
impedance load
Balanced 3p source
  Equal in magnitude, 120 deg difference in phase
Balanced 3p impedance load
  Identical impedances

## Slide 64: Balanced 3-phase system
voltage
source
transmission line
impedance
load
Balanced 3p operation
  Balanced 3p sources
  Balanced 3p loads
  Balanced (identical) transmission lines

## Slide 65: Advantages
1-phase
3-phase

## Slide 66: Advantages
1-phase
3-phase

## Slide 67: Advantages
1-phase
3-phase
Advantages of balanced 3p operation
  Instantaneous power is constant in t !
  Uses ~1/2 as much materials (wires) as three 1p system
  Incurs ~1/2 as much active power loss as three 1p system
=

## Slide 68: 3-phase AC : 3 key ideas
  Phasor representation
  Balanced operation
  Per-phase analysis

## Slide 69: Per-phase analysis: Wye
Important properties of balanced 3p system

## Slide 70: Per-phase analysis: Wye
Important properties of balanced 3p system
  All voltages and currents are 3-phase balanced
  Phases are decoupled, i.e., variables in each phase depend only on quantities in that phase

## Slide 71: Per-phase analysis: Wye
Properties:
  All voltages and currents are 3-phased balanced
  Phases are decoupled
...
...
per-phase equivalent circuit

## Slide 72: Delta-Wye transformation
Equivalent 3p sources: same external behavior
line-to-line voltages:

## Slide 73: Delta-Wye transformation
Equivalent 3p sources: same external behavior
line-to-line voltages:

## Slide 74: Delta-Wye transformation
Equivalent 3p sources: same external behavior
same terminal currents on same line-to-line voltages

## Slide 75: Per-phase analysis
voltage
source
transmission line
impedance
load
  Convert all Delta sources and loads into Wye
  Solve phase a circuit with all neutrals connected for desired variables
  Phase b / c variables: subtract / add 120deg to phase a variables
  If variables internal to Delta configurations are desired, solve them from original circuit

## Slide 76: Per-phase analysis
voltage
source
transmission line
impedance
load
phase-a
circuit

## Slide 77: Per-phase analysis
voltage
source
transmission line
impedance
load
phase-a
circuit

## Slide 78: Recap: basic concepts
3-phase AC transmission system
  Phasor representation
  Balanced operation
  Per-phase analysis
We will describe device and network models, and analyze
them, in phasor domain, using per-phase analysis

## Slide 79: The flow of power I
Why smart grid? (15 mins)
Three-phase AC transmission: 3 key ideas (30 mins)
  Phasor representation
  Balanced operation
  Per-phase analysis
Device models (30 mins)
  Transmission line
  Transformer
  Generator
Basic concepts and models

## Slide 80: Transmission line model
model of transmission line
  Terminal behavior
  What do line parameters depend on ?
  What about a 3-phase line ?
  What are some implications ?
series impedance
shunt
admittance

## Slide 81: Transmission line model
Line inductance l
Multiple conductors
total flux linkages
self inductance
mutual inductance

## Slide 82: Transmission line model
Conditions
  Symmetric 3-phase line
Multiple conductors
“self-inductance”
The phases are decoupled !

## Slide 83: Transmission line model
Line capacitance c
Multiple conductors
self inductance
mutual inductance
total charge / m

## Slide 84: Transmission line model
Conditions
  Symmetric 3-phase line
Multiple conductors
“self-capacitance”
The phases are decoupled !

## Slide 85: Transmission line model
Line parameters (balanced 3p line)
  Phases are decoupled
  Line inductance and capacitance
  Line resistance r / conductance g depend on wire material & size

## Slide 86: Transmission line model
per-phase model of phase voltage:

## Slide 87: Transmission line model
per-phase model of phase voltage:

## Slide 88: Transmission line model
model of transmission line
series impedance
shunt
admittance

## Slide 89: Transmission line model
Long line (l>150mi):
Long line (50<l<150mi):
Long line (l<50mi):

## Slide 90: Transmission line model
High voltage min transmission line loss
Specified: required load power and voltage

## Slide 91: Transmission line model
Recap
  Line characteristics depend on materials, size, and geometry of 3-phase line
  Linear per-phase circuit model
  circuit model: series impedance + shunt admittance

## Slide 92: The flow of power I
Why smart grid? (15 mins)
Three-phase AC transmission: 3 key ideas (30 mins)
  Phasor representation
  Balanced operation
  Per-phase analysis
Device models (30 mins)
  Transmission line
  Transformer
  Generator
Basic concepts and models

## Slide 93: Transformer model
Single-phase ideal transformer n

## Slide 94: Transformer model
Single-phase (non-ideal) transformer
can be easily measured

## Slide 95: Transformer model
Single-phase (non-ideal) transformer

## Slide 96: Transformer model
3-phase ideal transformer

## Slide 97: Transformer model
3-phase ideal transformer
per-phase properties

## Slide 98: Transformer model
3-phase ideal transformer
per-phase properties

## Slide 99: Transformer model
3-phase ideal transformer
per-phase properties

## Slide 100: Transformer model
3-phase ideal transformer
per-phase properties

## Slide 101: Transformer model
Per-phase equivalent circuit

## Slide 102: Transformer model
Recap
  Four configurations: YY, DD, DY, YD
  Linear per-phase circuit model

## Slide 103: Generator model

## Slide 104: Putting everything together
3p generator
(terminal
voltage)
3p transformer
(stepup)
3p transmission
line
3p transformer
(stepdown)

## Slide 105: Putting everything together
single-phase equivalent circuit

## Slide 106: The flow of power II
Network models (10mins)
  Admittance matrix
  Power flow models
Optimal power flow problems (35mins)
  Formulation and example
  Convex relaxations
  Real-time OPF
Power flow and optimization

## Slide 107: Example circuit model

## Slide 108: Network model
Each line modeled as model
Series impedance
Shunt admittance at each end
They may not be equal

## Slide 109: Network admittance matrix
Y : network graph + admittances

## Slide 110: Network admittance matrix

## Slide 111: The flow of power II
Network models (10mins)
  Admittance matrix
  Power flow models
Optimal power flow problems (35mins)
  Formulation and example
  Convex relaxations
  Real-time OPF
Power flow and optimization

## Slide 112: Bus injection model
i
j
k
admittance matrix:
graph G: undirected
Y specifies topology of G and
impedances z on lines

## Slide 113: Bus injection model
admittance matrix:
power balance
Kirchhoff law

## Slide 114: Bus injection model
power balance
Kirchhoff law
Eliminate I :

## Slide 115: Bus injection model
Complex form:
Polar form:
Cartesian form:

## Slide 116: Bus injection model
DC power flow
Assumptions:
Lossless short line
Small angle difference
Fixed voltage magnitude
Ignore reactive power

## Slide 117: Branch flow model
power definition
power balance
Kirchhoff law
loss
sending
end pwr
sending
end pwr

## Slide 118: Recap
Branch flow model
Bus injection model
solution
set

## Slide 119: Equivalence
solution
set
Theorem:
BIM and BFM are equivalent in this sense
Any result in one model is in principle provable in the other,
… but some results are easier to formulate or prove in one
than the other

## Slide 120: BFM for radial networks
Reduces to DistFlow model of Baran-Wu 1989
  Efficient solution: forward-backward sweep
  Linear model more suitable for distribution system
  Explicit solution for linear model
  Simple analytical bounds on nonlinear DistFlow model
Extension to multiphase unbalanced model
  Much more numerically stable

## Slide 121: The flow of power II
Network models (10mins)
  Admittance matrix
  Power flow models
Optimal power flow problems (35mins)
  Formulation and example
  Convex relaxations
  Real-time OPF
Power flow and optimization

## Slide 122: Optimal power flow (OPF)
OPF is solved routinely for
  network control & optimization decisions
  market operations & pricing
  at timescales of mins, hours, days, …
Non-convex and hard to solve
  Huge literature since 1962
  Common practice: DC power flow (LP)
  Also: Newton-Raphson, interior point, …

## Slide 123: Optimal power flow
describes network topology and impedances
is net power injection (generation) at node j
power flow equation
gen cost, power loss
line flow
injection limits
line limits
voltage limits

## Slide 124: Optimal power flow
power flow equation
gen cost, power loss
line flow
injection limits
line limits
voltage limits
nonconvex feasible set (nonconvex QCQP)
not Hermitian (nor positive semidefinite)
is positive semidefinite (and Hermitian)

## Slide 125: Optimal power flow
Ian Hiskens, Michigan
OPF problem underlies numerous applications
nonlinearity of power flow equations  nonconvexity

## Slide 126: Dealing with nonconvexity
Linearization
  DC approximation
Convex relaxations
  Semidefinite relaxation (Lasserre hierarchy)
  QC relaxation (van Hentenryck)
  Strong SOCP (Sun)

## Slide 127: Dealing with nonconvexity
Linearization
  DC approximation
Convex relaxations
  Semidefinite relaxation (Lasserre hierarchy)
  QC relaxation (van Hentenryck)
  Strong SOCP (Sun)
Realtime OPF
  Online algorithm, as opposed to offline
  Also tracks time-varying OPF

## Slide 128
Relaxations of AC OPF
dealing with nonconvexity
Low, Convex relaxation of OPF, 2014
http://netlab.caltech.edu
Bose (UIUC)
Chandy
Farivar (Google)
Gan (FB)
Lavaei (UCB)
many others at & outside Caltech …
Li (Harvard)

## Slide 129: Equivalent feasible sets
Equivalent problem:
convex in W
except this constraint
quadratic in V
linear in W

## Slide 130: Solution strategy
If optimal solution satisfies easily checkable conditions, then optimal solution of OPF can be recovered

## Slide 131: Equivalent relaxations
For radial networks: always solve SOCP !
Theorem
  Radial G: SOCP is equivalent to SDP ( )
  Mesh G: SOCP is strictly coarser than SDP

## Slide 132: Exact relaxation
For radial networks, sufficient conditions on
  power injections bounds, or
  voltage upper bounds, or
  phase angle bounds

## Slide 133: Exact relaxation
For radial networks, sufficient conditions on
  power injections bounds, or
  voltage upper bounds, or
  phase angle bounds

## Slide 134: Exact relaxation
graph of QCQP
QCQP
QCQP over tree

## Slide 135: Exact relaxation
Key condition
QCQP
Theorem
SOCP relaxation is exact for
QCQP over tree
Bose et al 2012, 2014
Sojoudi, Lavaei 2013

## Slide 136: Implication on OPF
Not both lower & upper bounds on real & reactive powers at both ends
of a line can be finite

## Slide 137: Example
power flow
solution X
SDP Y
SOCP Y
Real Power
Reactive Power
Relaxation is exact if X and Y have same Pareto front
SOCP is faster but coarser than SDP
Bose, Low, Teeraratkul, Hassibi TAC 2015

## Slide 138: Potential benefits
SDP
cost
MATPOWER cost
IEEE test
systems
12.4% lower cost than solution from nonlinear solver MATPOWER
[Louca, Seiler, Bitar 2013]

## Slide 139: Potential benefits
Case study on an SCE feeder
  Southern California
  1,400 residential houses, ~200 commercial buildings
  Controllable loads: EV, pool pumps, HVAC, PV inverters
  Formulated as an OPF problem, multiphase unbalanced radial network
optimized
baseline
peak load reduction: 8%
energy cost reduction: 4%

## Slide 140
Dvijotham (DeepMind)
Realtime AC OPF
for tracking
Gan (FB)
Tang (Caltech)
Gan & L, JSAC 2016
Tang et al, TSG 2017
See also: Dall’Anese et al, Bernstein et al,
Hug & Dorfler et al, Callaway et al

## Slide 141: Motivations
Simplify OPF simulation/solution
  Solving static OPF with simulator in the loop
  Avoid modifying GridLab-D during ARPA-E GENI (2012-15)
Deal with nonconvexity
  Network computes power flow solutions in real time at scale for free
  Exploit it for our optimization/control
Track optimal solution of time-varying OPF
  Uncertainty will continue to increase
  Real-time measurements increasingly become available on seconds timescale
  Must, and can, close the loop in the future

## Slide 142: Dealing with nonconvexity
Linearization
  DC approximation
Convex relaxations
  Semidefinite relaxation (Lasserre hierarchy)
  QC relaxation (van Hentenryck)
  Strong SOCP (Sun)
Realtime OPF
  Online algorithm, as opposed to offline
  Also tracks time-varying OPF

## Slide 143: Literature
Static OPF:
Gan and Low, JSAC 2016
Dall’Anese, Dhople and Giannakis, TPS 2016
Arnold et al, TPS 2016
A. Hauswirth, et al, Allerton 2016
Time-varying OPF:
Dall’Anese and Simonetto, TSG 2016
Wang et al, TPS 2016
Tang, Dvijotham and Low, TSG 2017
Tang and Low, CDC 2017
Earlier relevant work on voltage control
Survey: Molzahn et al, TSG 2017

## Slide 144: OPF
power flow equations
operational constraints
capacity limits
controllable
devices
uncontrollable
state

## Slide 145: OPF
power flow equations
operational constraints
capacity limits

## Slide 146: OPF
power flow equations
operational constraints
capacity limits

## Slide 147: OPF: eliminate y
Theorem [Huang, Wu, Wang, & Zhao. TPS 2016]
For DistFlow model, controllable (feasible) region
is convex (despite nonlinearity of y(x))

## Slide 148: OPF: add barrier or penalty
f: nonconvex
add barrier or penalty function
to remove operational constraints

## Slide 149: Online (feedback) perspective
control
x(t)
measurement,
communication
y(t)
physical
network
cyber
network
Explicitly exploits network as power flow solver
Naturally tracks changing network conditions

## Slide 150
control
u(t)
measurement
x(t)
physical
network
cyber
network

## Slide 151: Outline: realtime OPF
Motivation
Problem formulation
Static OPF
  1st order algorithm
  Optimality properties
Time-varying OPF
  2nd order algorithm
  Tracking performance
  Distributed implementation
[Gan & Low, JSAC 2016]
[Tang, Dj, & Low, TSG 2017]
[Tang & Low, CDC 2017]

## Slide 152: Static OPF
gradient projection algorithm:
active control
law of physics
[Gan & Low, JSAC 2016]

## Slide 153: Local optimality
Under appropriate assumptions
  x(t) converges to set of local optima
  if #local optima is finite, x(t) converges

## Slide 154: Global optimality
Theorem
If co{local optima} are in A then
  x(t) converges to the set of global optima
  x(t) itself converges a global optimum if #local optima is finite

## Slide 155: Global optimality
Theorem
  If SOCP is exact over X, then assumption holds
Incidentally, this turns out to be the convergence condition in Arnold,et al, “Model-Free Optimal Control of
VAR Resources in Distribution Systems: An Extremum Seeking Approach,”

## Slide 156: Suboptimality gap
  Informally, a local minimum is almost as good
  as any strictly interior feasible point
any local
optimum
any original
feasible pt
slightly away
from X boundary

## Slide 157: Simulations

## Slide 158: Outline: realtime OPF
Motivation
Problem formulation
Static OPF
Dynamic OPF
  2nd order algorithm
  Tracking performance
  Distributed implementation
[Gan & Low, JSAC 2016]
[Tang, Dj, & Low, TSG 2017]
[Tang & Low, CDC 2017]
See also: Dall’Anese and Simonetto, TSG 2016
Wang et al, TPS 2016

## Slide 159: Tracking performance
realtime OPF algorithms can track time-varying OPF well
IEEE 300 bus

## Slide 160: Tracking performance
realtime OPF algorithms can track time-varying OPF well
IEEE 300 bus

## Slide 161: Drifting OPF
drifting
OPF
static
OPF

## Slide 162: Drifting OPF
active control
law of physics
Quasi-Newton algorithm:
[Tang, Dj & Low, 2017]

## Slide 163: Drifting OPF
e.g. approx Hessian
[Tang, Dj & Low, 2017]
Computing by solving convex QP:

## Slide 164: Tracking performance
Theorem
avg rate of drifting
control error

## Slide 165: Tracking performance
Theorem
avg rate of drifting
of optimal solution
of feasible set
[Tang, Dj, & Low, TSG 2017]

## Slide 166: Tracking performance
Theorem
error in Hessian approx
[Tang, Dj, & Low, TSG 2017]

## Slide 167: Tracking performance
Theorem
“condition number” of Hessian
[Tang, Dj, & Low, TSG 2017]

## Slide 168: Tracking performance
Theorem
cost of Alg
optimal cost
dynamic
regret
rate of
drifting
subopt of
local min

## Slide 169: Tracking performance
Theorem
cost of Alg
optimal cost
dynamic
regret
rate of
drifting
subopt of
local min
first-order alg

## Slide 170: 2. Tracking performance
cost of Alg
optimal cost
dynamic
regret
Theorem
  If rate of drifting is then per-step
is asymptotically bounded by
  Can made arbitrarily small at cost of computation
(local min)

## Slide 171: Implementation
Implement L-BFGS-B
  More scalable
  Handles (box) constraints X
Simulations
  IEEE 300 bus

## Slide 172: Tracking performance
IEEE 300 bus

## Slide 173: Tracking performance
IEEE 300 bus

## Slide 174: Key message
Large network of DERs
  Real-time optimization at scale
  Computational challenge: power flow solution
Online optimization [feedback control]
  Network computes power flow solutions in real time at scale for free
  Exploit it for our optimization/control
  Naturally adapts to evolving network conditions
Examples
  Slow timescale: OPF
  Fast timescale: frequency control