## Slide 1: Branch Flow Model relaxations, convexification
Masoud Farivar Steven Low
Computing + Math Sciences
Electrical Engineering
Caltech
May 2012
Notes: Branch Flow Model: relaxations, convexification, computation
May 24, 2012: Optimization and Control for Smart Grids, 32nd CNLS Annual Conference, Santa Fe, NM (Misha Chertkov)
June 11, 2012: Greenmetrics Workshop, London, UK (Adam Wierman)
June 26, 2012: FERC Conference, Washington D.C. (Dick O’Neil)
July 31, 2012: Energy Day, Chinese University of Hong Kong (Minghua Chen)
Aug 2, 2012: HK University of Science & Technology (Vince Lau, Roger)
Aug 3, 2012: Hong Kong University, EE Dept, HK (Victor Li)
Aug 6, 2012: Tsinghua University, Institute of Theoretical Computer Science, Beijing, China (Raymond Yeung)
Aug 17, 2012: Zhejiang University, EE Dept, Hang Zhou, China (Jiming Chen)
Aug 20, 2012: Shanghai Jiaotong University, EE Dept, Shanghai, China (Xinbing Wang)
Sept 2012: Melbourne University, NICTA, Australia (Pascal Van Hentenryck)
Sept 2012: Swinburne University, Australia (Lachlan Andrew)

## Slide 2: Acks and refs
Collaborators
  S. Bose, M. Chandy, L. Gan, D. Gayme, J. Lavaei, L. Li
BFM reference
  Branch flow model: relaxations and convexification
  M. Farivar and S. H. Low
  arXiv:1204.4865v2, April 2012
Other references
  Zero duality gap in OPF problem
  J. Lavaei and S. H. Low
  IEEE Trans Power Systems, Feb 2012
  QCQP on acyclic graphs with application to power flow
  S. Bose, D. Gayme, S. H. Low and M. Chandy
  arXiv:1203.5599v1, March 2012

## Slide 3: big picture

## Slide 4: Global trends
1 Proliferation renewables
  Driven by sustainability
  Enabled by policy and investment

## Slide 5: Sustainability challenge
US CO2 emission
Elect generation: 40%
Transportation: 20%
Electricity generation 1971-2007
1973:
6,100 TWh
2007:
19,800 TWh
Sources: International Energy Agency, 2009
DoE, Smart Grid Intro, 2008
In 2009, 1.5B people
have no electricity

## Slide 6
Source: Renewable Energy
Global Status Report, 2010
Source: M. Jacobson, 2011
Wind power over land (exc. Antartica)
70 – 170 TW
Solar power over land
340 TW
Worldwide
energy demand:
16 TW
electricity demand:
2.2 TW
wind capacity (2009):
159 GW
grid-tied PV capacity (2009):
21 GW
Notes: World wind speed at 100m:
All wind worldwide: 1,700 TW
All wind over land in high-wind areas outside Antartica: 70 – 170 TW
World power (all energy) demand in 2030: 16.9 TW
World surface solar
All solar worldwide: 6,500 TW
All solar over land in high-solar locations: 340 TW
Source: Renewable Energy Global Status Report, Sept 2010:
2009 grid-tied solar PV capacity increase
The world added 7GW of grid-connected PV capacity, to a total of 21 GW
Germany: +3.8 GW to a total of 9.8 GW
Spain: +70MW to a total of 3.4 GW (Govt subsidy expired!)
US: +470MW to a total of 1 GW (CA ~half of increase)
Off-grid capacity: 4 GW
2009 wind capacity increase
Wind power increased the most among all renewables, by 38 GW to a total of 159 GW
US: +10 GW to a total of 35 GW
China: +13.8 GW to a total of 25.8 GW
Germany: +1.9GW to a total of 25.8 GW

## Slide 7: Uncertainty
High Levels of Wind and Solar PV Will Present an Operating Challenge!
Source: Rosa Yang, EPRI

## Slide 8: Global trends
1 Proliferation of renewables
  Driven by sustainability
  Enabled by policy and investment
2 Migration to distributed arch
  2-3x generation efficiency
  Relief demand on grid capacity

## Slide 9: Large active network of DER
DER: PVs, wind turbines, batteries, EVs, DR loads

## Slide 10: Large active network of DER
DER: PVs, wind turbines, EVs, batteries, DR loads
Millions of active endpoints introducing rapid large
random fluctuations
in supply and demand

## Slide 11: Implications
Current control paradigm works well today
  Low uncertainty, few active assets to control
  Centralized, open-loop, human-in-loop, worst-case preventive
  Schedule supplies to match loads
Future needs
  Fast computation to cope with rapid, random, large fluctuations in supply, demand, voltage, freq
  Simple algorithms to scale to large networks of active DER
  Real-time data for adaptive control, e.g. real-time DR

## Slide 12: Key challenges
Nonconvexity
  Convex relaxations
Large scale
  Distributed algorithms
Uncertainty
  Risk-limiting approach

## Slide 13: Why is convexity important
Foundation of LMP
  Convexity justifies the use of Lagrange multipliers as various prices
  Critical for efficient market theory
Efficient computation
  Convexity delineates computational efficiency and intractability
A lot rides on (assumed) convexity structure
engineering, economics, regulatory

## Slide 14: optimal power flow motivations

## Slide 15: Optimal power flow (OPF)
OPF is solved routinely to determine
  How much power to generate where
  Market operation & pricing
  Parameter setting, e.g. taps, VARs
Non-convex and hard to solve
  Huge literature since 1962
  Common practice: DC power flow (LP)

## Slide 16: Optimal power flow (OPF)
Problem formulation
  Carpentier 1962
Computational techniques
  Dommel & Tinney 1968
  Surveys: Huneault et al 1991, Momoh et al 2001, Pandya et al 2008
Bus injection model: SDP relaxation
  Bai et al 2008, 2009, Lavaei et al 2010, 2012
  Bose et al 2011, Zhang et al 2011, Sojoudi et al 2012
  Lesieutre et al 2011
Branch flow model: SOCP relaxation
  Baran & Wu 1989, Chiang & Baran 1990, Taylor 2011, Farivar et al 2011

## Slide 17: Application: Volt/VAR control
Motivation
  Static capacitor control cannot cope with rapid random fluctuations of PVs on distr circuits
Inverter control
  Much faster & more frequent
  IEEE 1547 does not optimize VAR currently (unity PF)

## Slide 18: Load and Solar Variation
Empirical distribution
of (load, solar) for Calabash

## Slide 19: Summary
More reliable operation
Energy savings

## Slide 20: theory relaxations and convexification

## Slide 21: Outline
Branch flow model and OPF
Solution strategy: two relaxations
  Angle relaxation
  SOCP relaxation
Convexification for mesh networks
Extensions

## Slide 22: Two models
i
j
k
branch
flow
bus
injection

## Slide 23: Two models
i
j
k
branch
current
bus
current

## Slide 24: Two models
Equivalent models of Kirchhoff laws
  Bus injection model focuses on nodal vars
  Branch flow model focuses on branch vars

## Slide 25: Two models
What is the model?
What is OPF in the model?
What is the solution strategy?

## Slide 26: let’s start with something familiar

## Slide 27: Bus injection model
admittance matrix:
Kirchhoff law
power balance
power definition

## Slide 28: Bus injection model
Kirchhoff law
power balance
power definition

## Slide 29: Bus injection model: OPF
e.g. quadratic gen cost
Kirchhoff law
power balance

## Slide 30: Bus injection model: OPF
e.g. quadratic gen cost
Kirchhoff law
power balance

## Slide 31: Bus injection model: OPF
e.g. quadratic gen cost
Kirchhoff law
power balance
nonconvex, NP-hard

## Slide 32: Bus injection model: OPF
In terms of V:
Key observation [Bai et al 2008]:
OPF = rank constrained SDP

## Slide 33: Bus injection model: OPF
convex relaxation: SDP

## Slide 34: Bus injection model: relaxation
convex relaxation: SDP
polynomial

## Slide 35: Bus injection model: SDR
Non-convex QCQP
Rank-constrained SDP
Relax the rank constraint and solve the SDP
Does the optimal solution satisfy the rank-constraint?
We are done!
Solution may not
be meaningful
yes
no
Lavaei 2010, 2012
Radial: Bose 2011, Zhang 2011
Sojoudi 2011
Lesiertre 2011
Bai 2008

## Slide 36: QCQP over tree
graph of QCQP
QCQP
QCQP over tree

## Slide 37: QCQP over tree
Semidefinite relaxation
QCQP

## Slide 38: QCQP over tree
Key condition
QCQP
Theorem
semidefinite relaxation is exact for
QCQP over tree
S. Bose, D. Gayme, S. H. Low and M. Chandy, March 2012

## Slide 39: QCQP over tree
Remarks
  condition implies constraint patterns
  full AC: inc real and reactive powers
  allows constraints on line flows, loss
Theorem
semidefinite relaxation is exact for
QCQP over tree
S. Bose, D. Gayme, S. H. Low and M. Chandy, March 2012
Key condition

## Slide 40: OPF over radial networks
full constraints violate key condition

## Slide 41: OPF over radial networks
“no lower bounds”
removes these

## Slide 42: OPF over radial networks
bounds on constraints
remove these

## Slide 43: OPF over radial networks
bounds on constraints
remove these

## Slide 44: Bus injection model: summary
OPF = rank constrained SDP
Sufficient conditions for SDP to be exact
  Whether a solution is globally optimal is always easily checkable
  Mesh: must solve SDP to check
  Tree: depends only on constraint pattern or r/x ratios

## Slide 45: Two models
What is the model?
What is OPF in the model?
What is the solution strategy?

## Slide 46: Branch flow model
Ohm’s law
power balance
sending
end pwr
loss
sending
end pwr
power def

## Slide 47: Branch flow model
Ohm’s law
power balance
branch flows
power def

## Slide 48: Branch flow model
Ohm’s law
power balance
power def

## Slide 49: Branch flow model: OPF
Kirchoff’s Law:
Ohm’s Law:
real power loss
CVR (conservation
voltage reduction)

## Slide 50: Branch flow model: OPF

## Slide 51: Branch flow model: OPF

## Slide 52: Branch flow model: OPF
branch flow
model
generation,
VAR control

## Slide 53: Branch flow model: OPF
branch flow
model
demand
response

## Slide 54: Outline
Branch flow model and OPF
Solution strategy: two relaxations
  Angle relaxation
  SOCP relaxation
Convexification for mesh networks
Extensions

## Slide 55: Solution strategy
OPF
nonconvex
OPF-ar
nonconvex
OPF-cr
convex
exact
relaxation
inverse
projection
for tree
angle
relaxation
SOCP
relaxation

## Slide 56: Angle relaxation
branch flow
model

## Slide 57: Angle relaxation
branch flow
model
eliminate
angles
points relaxed
to circles !

## Slide 58: Angle relaxation

## Slide 59: Angle relaxation

## Slide 60: Angle relaxation

## Slide 61: Relaxed BF model
Baran and Wu 1989
for radial networks
relaxed branch flow solutions: satisfy

## Slide 62: OPF
branch flow
model

## Slide 63: OPF

## Slide 64: OPF-ar
relax each voltage/current from a
point in complex plane into a circle

## Slide 65: OPF-ar
convex objective
linear constraints
quadratic equality
source of
nonconvexity

## Slide 66: OPF-cr
 inequality

## Slide 67: OPF-cr
relax to convex hull
(SOCP)

## Slide 68: Recap so far …
OPF
nonconvex
OPF-ar
nonconvex
OPF-cr
convex
exact
relaxation
inverse
projection
for tree
angle
relaxation
SOCP
relaxation

## Slide 69: OPF-cr is exact relaxation
Theorem
OPF-cr is convex
  SOCP when objective is linear
  SOCP much simpler than SDP
OPF-cr is exact
  optimal of OPF-cr is also optimal for OPF-ar
  for mesh as well as radial networks
  real & reactive powers, but volt/current mags

## Slide 70: Angle recovery
OPF ??
OPF-ar
does there exist s.t.

## Slide 71: Angle recovery
Theorem
solution to OPF recoverable from iff
inverse projection exist iff s.t.
Two simple angle recovery algorithms
  centralized: explicit formula
  decentralized: recursive alg
incidence matrix;
depends on topology
depends on
OPF-ar solution

## Slide 72: Angle recovery
Theorem
For radial network:
mesh
tree

## Slide 73: Angle recovery
Theorem
Inverse projection exist iff
Unique inverse given by
For radial network:
#buses - 1
#lines in T
#lines outside T

## Slide 74: OPF solution
Solve OPF-cr
OPF solution
Recover angles
radial
SOCP
explicit formula
distributed alg

## Slide 75: OPF solution
Solve OPF-cr
???
N
OPF solution
Recover angles
radial
angle recovery
condition holds?
Y
mesh

## Slide 76: Outline
Branch flow model and OPF
Solution strategy: two relaxations
  Angle relaxation
  SOCP relaxation
Convexification for mesh networks
Extensions

## Slide 77: Recap: solution strategy
OPF
nonconvex
OPF-ar
nonconvex
OPF-cr
convex
exact
relaxation
inverse
projection
for tree
angle
relaxation
SOCP
relaxation
??

## Slide 78: Phase shifter
ideal phase shifter

## Slide 79: Convexification of mesh networks
OPF
Theorem
Need phase shifters only
outside spanning tree
OPF-ar
OPF-ps
optimize over phase shifters as well

## Slide 80: Angle recovery with PS
Theorem
Inverse projection always exists
Unique inverse given by
Don’t need PS in spanning tree

## Slide 81: OPF solution
Solve OPF-cr
Optimize phase
shifters
N
OPF solution
Recover angles
radial
angle recovery
condition holds?
Y
mesh
explicit formula
distributed alg

## Slide 82: Examples
With PS

## Slide 83: Examples
With PS

## Slide 84: Key message
Radial networks computationally simple
  Exploit tree graph & convex relaxation
  Real-time scalable control promising
Mesh networks can be convexified
  Design for simplicity
  Need few (?) phase shifters (sparse topology)

## Slide 85: Outline
Branch flow model and OPF
Solution strategy: two relaxations
  Angle relaxation
  SOCP relaxation
Convexification for mesh networks
Extensions

## Slide 86: Extension: equivalence
Work in progress with Subhonmesh Bose, Mani Chandy
Theorem
BI and BF model are equivalent
(there is a bijection between and )

## Slide 87: Extension: equivalence
Work in progress with Subhonmesh Bose, Mani Chandy
Theorem: radial networks
in SOCP W in SDR
satisfies angle cond W has rank 1
SDR
SOCP

## Slide 88: Extension: distributed solution
Work in progress with Lina Li, Lingwen Gan, Caltech
Local algorithm at bus j
update local variables based on Lagrange multipliers from children
send Lagrange multipliers to parents
i
local Lagrange multipliers
local load, generation
highly parallelizable !

## Slide 89: Extension: distributed solution
Work in progress with Lina Li, Lingwen Gan, Caltech
Theorem
Distributed algorithm converges
  to global optimal for radial networks
  to global optimal for convexified mesh networks
  to approximate/optimal for general mesh networks
45
0
0.1
0.2
0.3
p (MW)
140
145
150
155
0
1
2
3
0
1000
2000
3000
4000
3
1.5
2
2.5
P0 (MW)
P (MW)
SCE distribution circuit